## Introduction
Sprecher+Schuh Functional Safety Data Sheet
About This Publication | Disclaimer of Warranty The information maintained in this document is provided ”as is” without warranties of any kind, either express or implied, including without limitation, all implied warranties of accuracy, merchantability, fitness for a particular purpose, non-infringement or other violation of rights. Sprecher+Schuh does not warrant or make any representations regarding the use, validity, accuracy, or reliability of, or the results of any use of, or otherwise respecting, the information maintained in or accessed by way of this document.
Limitation of Liability Under no circumstance (including negligence and to the fullest extend permitted by applicable law) will Sprecher+Schuh be liable for any direct, indirect, special, incidental, punitive or consequential damages (including without limitation, business interruption, delays, loss of data or profit) arising out of the use or the inability to use the information maintained in or accessed by way of this document even if Sprecher+Schuh has been advised of the possibility of such damages. If use of such information results in the need for servicing, repair or correction of user equipment or data, user assumes any costs associated therewith.
| Please review important Legal Notices with regard to the Rockwell Automation SISTEMA Libraries. See publication: | SAFETY-RN001
Allen-Bradley, ArmorBlock, ArmorStart, Cadet, Compact 5000, CompactBlock, CompactLogix, Elf, expanding human possibility, Ferrogard, FLEX 5000, Guard I/O, GuardLink, GuardLogix, Guardmaster, GuardPLC, GuardShield, Kinetix, Lifeline, Logix5000, MatGuard, MobileView, POINT Guard I/O, PowerFlex, ProSafe, RightSight, Rockwell Automation, Rotacam, RSLogix 5000, SafeZone, Safedge, SensaGuard, Series 9000, Sipha, SmartGuard, Trojan, VisiSight, WorldProx, and Zero-Force Touch Buttons are trademarks of Rockwell Automation, Inc. EtherNet/IP and CIP Safety are trademarks of ODVA, Inc. Trademarks not belonging to Rockwell Automation are property of their respective companies.
Publication SAFETY-SR001J-EN-E - June 2022 (Sprecher+Schuh)
Supersedes Publication SAFETY-SR001I-EN-E - February 2017 |  | Copyright © 2022 Rockwell Automation Inc. All Rights Reserved . Printed in USA.

## VDMA
Device Name | Use Case Hierarchy | Part Number | B10D | PL | SIL | Category | PFHD | TMT1 | Use Case Notes | VDMA Device Type | Device Group | Description | Revision | Function | MTTFD | MTTF | RDF | B10 | DC | λDD | DFR | DTI | λDU | HFT | MTBF | PFDavg | λSD | SFF | λS | SRT | STR | λSU | T1 | TFR
Control Relay: CSS7: | Mechanical Load | CSS7-* | [5 empty] | 20 | 1) B10d value assuming a failure to open is considered a dangerous failure. B10d value calculated with AC 3 motor. 2) Category 1 applies where the combination of the usage rate and the B10D value results in an MTTFd equal to or greater than 30 years. 3) The DC value given is for the device used on its own with no additional monitoring/diagnostic equipment. An increased value for DC can be achieved by direct monitoring, that is, connection of the mechanically linked auxiliary contacts to external monitoring equipment. In most cases, redundant devices or a second switch-off path this will be required. It assumes a maximum diagnostic test interval of 6 months. It assumes the monitoring of all dangerous single fault modes. The maximum value given will not be achievable if it can be foreseen that some single faults will not be detected. | Device Type 3 | Relay |  |  | Logic, Output |  |  | 50 | 15000000
Control Relay: CSS7: | AC15 | CSS7-* | [5 empty] | 20 | 1) B10d value assuming a failure to open is considered a dangerous failure. B10d value calculated with AC 3 motor. 2) Category 1 applies where the combination of the usage rate and the B10D value results in an MTTFd equal to or greater than 30 years. 3) The DC value given is for the device used on its own with no additional monitoring/diagnostic equipment. An increased value for DC can be achieved by direct monitoring, that is, connection of the mechanically linked auxiliary contacts to external monitoring equipment. In most cases, redundant devices or a second switch-off path will be required. It assumes a maximum diagnostic test interval of 6 months. It assumes the monitoring of all dangerous single fault modes. The maximum value given will not be achievable if it can be foreseen that some single faults will not be detected. | Device Type 3 | Relay |  |  | Logic, Output |  |  | 50 | 1500000
E-Stop Switch: D7D-MT 22mm | Pull to release | D7D-MT44 | 111000 |  |  |  |  | 20 | 1) B10d data given is based on a failure of either channel. It can be used to determine the MTTFd of each single channel. 2) The data given is based on some use of fault exclusion in accordance with EN ISO 13849-2:2012 Table A4. 3) The DC or SFF value given is for the device used on its own with no additional monitoring/diagnostic equipment. An increased value for DC and SFF can be achieved by connection to specified external monitoring equipment. 4) Use the lowest value of Mission Time or T10d for calculation. 5) Load conditions - 20 mA/24V DC, confidence factor 90% Report-No.: 968/EL 660.01/10 | Device Type 3 | Emergency Stop Device |  |  | Input | [18 empty] | 175200
E-Stop Switch: D7D-MT 22mm | Twist to release | D7D-MT44 | 138000 |  |  |  |  | 20 | 1) B10d data given is based on a failure of either channel. It can be used to determine the MTTFd of each single channel. 2) The data given is based on some use of fault exclusion in accordance with EN ISO 13849-2:2012 Table A4. 3) The DC or SFF value given is for the device used on its own with no additional monitoring/diagnostic equipment. An increased value for DC and SFF can be achieved by connection to specified external monitoring equipment. 4) Use the lowest value of Mission Time or T10d for calculation. 5) Load conditions - 20 mA/24V DC, confidence factor 90% Report-No.: 968/EL 660.01/10 | Device Type 3 | Emergency Stop Device |  |  | Input
E-Stop Switch:D7P/D7M 22mm | Pull to release, illuminated | D7P-LMP*, D7M-LMP* | 243000 |  |  |  |  | 20 | 1) B10d data given is based on a failure of either channel. It can be used to determine the MTTFd of each single channel. 2) The data given is based on some use of fault exclusion in accordance with EN ISO 13849-2:2012 Table A4. 3) The DC or SFF value given is for the device used on its own with no additional monitoring/diagnostic equipment. An increased value for DC and SFF can be achieved by connection to specified external monitoring equipment. 4) Use the lowest value of Mission Time or T10d for calculation. 5) Load conditions - 20 mA/24V DC, confidence factor 90% Report-No.: 968/EL 660.01/10 | Device Type 3 | Emergency Stop Device |  |  | Input | [18 empty] | 175200
E-Stop Switch: D7P/D7M 22mm | Twist to release, illuminated | D7P-LMT*, D7M-LMT* | 206000 |  |  |  |  | 20 | 1) B10d data given is based on a failure of either channel. It can be used to determine the MTTFd of each single channel. 2) The data given is based on some use of fault exclusion in accordance with EN ISO 13849-2:2012 Table A4. 3) The DC or SFF value given is for the device used on its own with no additional monitoring/diagnostic equipment. An increased value for DC and SFF can be achieved by connection to specified external monitoring equipment. 4) Use the lowest value of Mission Time or T10d for calculation. 5) Load conditions - 20 mA/24V DC, confidence factor 90% Report-No.: 968/EL 660.01/10 | Device Type 3 | Emergency Stop Device |  |  | Input | [18 empty] | 175200
E-Stop Switch: D7P/D7M 22mm | Key release | D7P-MK*, D7M-MK* | 2010000 |  |  |  |  | 20 | 1) B10d data given is based on a failure of either channel. It can be used to determine the MTTFd of each single channel. 2) The data given is based on some use of fault exclusion in accordance with EN ISO 13849-2:2012 Table A4. 3) The DC or SFF value given is for the device used on its own with no additional monitoring/diagnostic equipment. An increased value for DC and SFF can be achieved by connection to specified external monitoring equipment. 4) Use the lowest value of Mission Time or T10d for calculation. 5) Load conditions - 20 mA/24V DC, confidence factor 90% Report-No.: 968/EL 660.01/10 | Device Type 3 | Emergency Stop Device |  |  | Input | [18 empty] | 175200
E-Stop Switch: D7P/D7M 22mm | Pull to release, non-illuminated | D7P-MP*, D7M-MP* | 243000 |  |  |  |  | 20 | 1) B10d data given is based on a failure of either channel. It can be used to determine the MTTFd of each single channel. 2) The data given is based on some use of fault exclusion in accordance with EN ISO 13849-2:2012 Table A4. 3) The DC or SFF value given is for the device used on its own with no additional monitoring/diagnostic equipment. An increased value for DC and SFF can be achieved by connection to specified external monitoring equipment. 4) Use the lowest value of Mission Time or T10d for calculation. 5) Load conditions - 20 mA/24V DC, confidence factor 90% Report-No.: 968/EL 660.01/10 | Device Type 3 | Emergency Stop Device |  |  | Input
E-Stop Switch: D7P/D7M 22mm | Twist to release, non-illuminated | D7P-MT*, D7M-MT* | 736000 |  |  |  |  | 20 | 1) B10d data given is based on a failure of either channel. It can be used to determine the MTTFd of each single channel. 2) The data given is based on some use of fault exclusion in accordance with EN ISO 13849-2:2012 Table A4. 3) The DC or SFF value given is for the device used on its own with no additional monitoring/diagnostic equipment. An increased value for DC and SFF can be achieved by connection to specified external monitoring equipment. 4) Use the lowest value of Mission Time or T10d for calculation. 5) Load conditions - 20 mA/24V DC, confidence factor 90% Report-No.: 968/EL 660.01/10 | Device Type 3 | Emergency Stop Device |  |  | Input
Output Contactor: CAS7-9…37: AC3 Load | Failure to open = dangerous fault | CAS7-9…37 at AC3 | [5 empty] | 20 | 1) B10 Data shown for AC3 Load. If other loading is used, refer to the load-life curves found in the product Technical Data. 2) B10 is known and 75% fail to open and 25% fail to close. B10d Fail to Open =B10x(1/75%), B10d Fail to Close =B10x(1/25%) 3) For Category greater than 1, diagnostic coverage must be supplied externally by direct monitoring of the mechanically linked auxiliary contacts. 4) Typical diagnostic test interval of 6 months. | Device Type 3 | Contactor |  |  | Output |  |  | 75 | 1300000
Output Contactor: CAS7-9…37: AC3 Load | Failure to close = dangerous fault | CAS7-9…37 at AC3 | [5 empty] | 20 | 1) B10 Data shown for AC3 Load. If other loading is used, refer to the load-life curves found in the product Technical Data. 2) B10 is known and 75% fail to open and 25% fail to close. B10d Fail to Open =B10x(1/75%), B10d Fail to Close =B10x(1/25%) 3) For Category greater than 1, diagnostic coverage must be supplied externally by direct monitoring of the mechanically linked auxiliary contacts. 4) Typical diagnostic test interval of 6 months. | Device Type 3 | Contactor |  |  | Output |  |  | 25 | 1300000
Output Contactor: CAS7-9…55: Mechanical | Failure to open = dangerous fault | CAS7-9…55 Mechanical | [5 empty] | 20 | 1) B10 Data shown is for no load, mechanical switching. 2) B10 is known and 50% fail to open and 50% fail to close. B10d Fail to Open =B10x(1/50%), B10d Fail to Close =B10x(1/50%) 3) For Category greater than 1, diagnostic coverage must be supplied externally by direct monitoring of the mechanically linked auxiliary contacts. 4) Typical diagnostic test interval of 6 months. | Device Type 3 | Contactor |  |  | Output |  |  | 50 | 13000000
Output Contactor: CAS7-9…55: Mechanical | Failure to close = dangerous fault | CAS7-9…55 Mechanical | [5 empty] | 20 | 1) B10 Data shown is for no load, mechanical switching. 2) B10 is known and 50% fail to open and 50% fail to close. B10d Fail to Open =B10x(1/50%), B10d Fail to Close =B10x(1/50%) 3) For Category greater than 1, diagnostic coverage must be supplied externally by direct monitoring of the mechanically linked auxiliary contacts. 4) Typical diagnostic test interval of 6 months. | Device Type 3 | Contactor |  |  | Output |  |  | 50 | 13000000
Output Contactor: CAS7-43, 60, 72, 85, 97: AC3 Load | Failure to open = dangerous fault | CAS7-43,60,72, 85, 97 at AC3 | [5 empty] | 20 | 1) B10 Data shown for AC3 Load. If other loading is used, refer to the load-life curves found in the product Technical Data. 2) B10 is known and 75% fail to open and 25% fail to close. B10d Fail to Open =B10x(1/75%), B10d Fail to Close =B10x(1/25%) 3) For Category greater than 1, diagnostic coverage must be supplied externally by direct monitoring of the mechanically linked auxiliary contacts. 4) Typical diagnostic test interval of 6 months. | Device Type 3 | Contactor |  |  | Output |  |  | 75 | 1000000
Output Contactor: CAS7-43, 60, 72, 85, 97: AC3 Load | Failure to close = dangerous fault | CAS7-43,60,72, 85, 97 at AC3 | [5 empty] | 20 | 1) B10 Data shown for AC3 Load. If other loading is used, refer to the load-life curves found in the product Technical Data. 2) B10 is known and 75% fail to open and 25% fail to close. B10d Fail to Open =B10x(1/75%), B10d Fail to Close =B10x(1/25%) 3) For Category greater than 1, diagnostic coverage must be supplied externally by direct monitoring of the mechanically linked auxiliary contacts. 4) Typical diagnostic test interval of 6 months. | Device Type 3 | Contactor |  |  | Output |  |  | 25 | 1000000
Output Contactor: CAS7-55: AC3 Load | Failure to open = dangerous fault | CAS7-55 at AC3 | [5 empty] | 20 | 1) B10 Data shown for AC3 Load. If other loading is used, refer to the load-life curves found in the product Technical Data. 2) B10 is known and 75% fail to open and 25% fail to close. B10d Fail to Open =B10x(1/75%), B10d Fail to Close =B10x(1/25%) 3) For Category greater than 1, diagnostic coverage must be supplied externally by direct monitoring of the mechanically linked auxiliary contacts. 4) Typical diagnostic test interval of 6 months. | Device Type 3 | Contactor |  |  | Output |  |  | 75 | 800000
Output Contactor: CAS7-55: AC3 Load | Failure to close = dangerous fault | CAS7-55 at AC3 | [5 empty] | 20 | 1) B10 Data shown for AC3 Load. If other loading is used, refer to the load-life curves found in the product Technical Data. 2) B10 is known and 75% fail to open and 25% fail to close. B10d Fail to Open =B10x(1/75%), B10d Fail to Close =B10x(1/25%) 3) For Category greater than 1, diagnostic coverage must be supplied externally by direct monitoring of the mechanically linked auxiliary contacts. 4) Typical diagnostic test interval of 6 months. | Device Type 3 | Contactor |  |  | Output |  |  | 25 | 800000
Output Contactor: CAS7-60 to 97: Mechanical | Failure to close = dangerous fault | CAS7-60…97 Mechanical | [5 empty] | 20 | 1) B10 Data shown is for no load, mechanical switching. 2) B10 is known and 50% fail to open and 50% fail to close. B10d Fail to Open =B10x(1/50%), B10d Fail to Close =B10x(1/50%) 3) For Category greater than 1, diagnostic coverage must be supplied externally by direct monitoring of the mechanically linked auxiliary contacts. 4) Typical diagnostic test interval of 6 months. | Device Type 3 | Contactor |  |  | Output |  |  | 50 | 6000000
Output Contactor: CAS7-60…97: Mechanical | Failure to open = dangerous fault | CAS7-60…97 Mechanical | [5 empty] | 20 | 1) B10 Data shown is for no load, mechanical switching. 2) B10 is known and 50% fail to open and 50% fail to close. B10d Fail to Open =B10x(1/50%), B10d Fail to Close =B10x(1/50%) 3) For Category greater than 1, diagnostic coverage must be supplied externally by direct monitoring of the mechanically linked auxiliary contacts. 4) Typical diagnostic test interval of 6 months. | Device Type 3 | Contactor |  |  | Output |  |  | 50 | 6000000
Output Contactor: CAS6-115 to 300 at AC3 - Without Electronic coil interface | Failure to open = dangerous fault | CAS6-115…300 at AC3 - Without Electronic coil interface | 1070000 |  |  |  |  | 20 | 1)The MTTFd value for the electronic controlled coil must be added as a separate block or element when the interface function is used. 2) B10d = failure to open = dangerous failure. 3) Category 1 applies where the combination of the usage rate and the B10D value results in an MTTFd equal to or greater than 30 years. 4) The DC value given is for the device used on its own with no additional monitoring/diagnostic equipment. An increased value for DC can be achieved by direct monitoring, that is, connection of the mechanically linked auxiliary contacts to external monitoring equipment. In most cases, redundant devices or a second switch-off path this will be required. It assumes a maximum diagnostic test interval of 6 months. It assumes the monitoring of all dangerous single fault modes. The maximum value given will not be achievable if it can be foreseen that some single faults will not be detected. 5) If using electronic coil add additional 100S-D***E electronic coil block to each channel using this block. (2 blocks) | Device Type 3 | Contactor |  |  | Output
Output Contactor: CAS6-420 at AC3 - Without Electronic coil interface | Standard | CAS7-420 at AC3 - Without Electronic coil interface | 800000 |  |  |  |  | 20 | 1)The MTTFd value for the electronic controlled coil must be added as a separate block or element when the interface function is used. 2) B10d = failure to open = dangerous failure. 3) Category 1 applies where the combination of the usage rate and the B10D value results in an MTTFd equal to or greater than 30 years. 4) The DC value given is for the device used on its own with no additional monitoring/diagnostic equipment. An increased value for DC can be achieved by direct monitoring, that is, connection of the mechanically linked auxiliary contacts to external monitoring equipment. In most cases, redundant devices or a second switch-off path this will be required. It assumes a maximum diagnostic test interval of 6 months. It assumes the monitoring of all dangerous single fault modes. The maximum value given will not be achievable if it can be foreseen that some single faults will not be detected. 5) If using electronic coil add additional 100S-D***E electronic coil block to each channel using this block. (2 blocks) | Device Type 3 | Contactor |  |  | Output
Output Contactor: CAUS7-9 to 37: AC3 Load | Failure to close = dangerous fault | CAUS7-9 to 37 at AC3 | [5 empty] | 20 | 1) B10 Data shown for AC3 Load. If other loading is used, refer to the load-life curves found in the product Technical Data. 2) B10 is known and 75% fail to open and 25% fail to close. B10d Fail to Open =B10x(1/75%), B10d Fail to Close =B10x(1/25%) 3) For Category greater than 1, diagnostic coverage must be supplied externally by direct monitoring of the mechanically linked auxiliary contacts. 4) Typical diagnostic test interval of 6 months. | Device Type 3 | Contactor |  |  | Output |  |  | 25 | 1300000 | [14 empty] | 175200
Output Contactor: CAUS7-9…37: AC3 Load | Failure to open = dangerous fault | CAUS7-9…37 at AC3 | [5 empty] | 20 | 1) B10 Data shown for AC3 Load. If other loading is used, refer to the load-life curves found in the product Technical Data. 2) B10 is known and 75% fail to open and 25% fail to close. B10d Fail to Open =B10x(1/75%), B10d Fail to Close =B10x(1/25%) 3) For Category greater than 1, diagnostic coverage must be supplied externally by direct monitoring of the mechanically linked auxiliary contacts. 4) Typical diagnostic test interval of 6 months. | Device Type 3 | Contactor |  |  | Output |  |  | 75 | 1300000 | [14 empty] | 175200
Output Contactor: CAUS7-9…55: Mechanical | Failure to open = dangerous fault | CAUS7-9…55 Mechanical | [5 empty] | 20 | 1) B10 Data shown is for no load, mechanical switching. 2) B10 is known and 50% fail to open and 50% fail to close. B10d Fail to Open =B10x(1/50%), B10d Fail to Close =B10x(1/50%) 3) For Category greater than 1, diagnostic coverage must be supplied externally by direct monitoring of the mechanically linked auxiliary contacts. 4) Typical diagnostic test interval of 6 months. | Device Type 3 | Contactor |  |  | Output |  |  | 50 | 13000000
Output Contactor: CAUS7-9…55: Mechanical | Failure to close = dangerous fault | CAUS7-9…55 Mechanical | [5 empty] | 20 | 1) B10 Data shown is for no load, mechanical switching. 2) B10 is known and 50% fail to open and 50% fail to close. B10d Fail to Open =B10x(1/50%), B10d Fail to Close =B10x(1/50%) 3) For Category greater than 1, diagnostic coverage must be supplied externally by direct monitoring of the mechanically linked auxiliary contacts. 4) Typical diagnostic test interval of 6 months. | Device Type 3 | Contactor |  |  | Output |  |  | 50 | 13000000
Output Contactor: CAUS7-43, 60, 72, 85, 97: AC3 Load | Failure to open = dangerous fault | CAUS7-43, 60, 72, 85, 97 at AC3 | [5 empty] | 20 | 1) B10 Data shown for AC3 Load. If other loading is used, refer to the load-life curves found in the product Technical Data. 2) B10 is known and 75% fail to open and 25% fail to close. B10d Fail to Open =B10x(1/75%), B10d Fail to Close =B10x(1/25%) 3) For Category greater than 1, diagnostic coverage must be supplied externally by direct monitoring of the mechanically linked auxiliary contacts. 4) Typical diagnostic test interval of 6 months. | Device Type 3 | Contactor |  |  | Output |  |  | 75 | 1000000
Output Contactor: CAUS7-43, 60, 72, 85, 97: AC3 Load | Failure to close = dangerous fault | CAUS7-43, 60, 72, 85, 97 at AC3 | [5 empty] | 20 | 1) B10 Data shown for AC3 Load. If other loading is used, refer to the load-life curves found in the product Technical Data. 2) B10 is known and 75% fail to open and 25% fail to close. B10d Fail to Open =B10x(1/75%), B10d Fail to Close =B10x(1/25%) 3) For Category greater than 1, diagnostic coverage must be supplied externally by direct monitoring of the mechanically linked auxiliary contacts. 4) Typical diagnostic test interval of 6 months. | Device Type 3 | Contactor |  |  | Output |  |  | 25 | 1000000
Output Contactor: CAUS7-55: AC3 Load | Failure to open = dangerous fault | CAUS7-55 at AC3 | [5 empty] | 20 | 1) B10 Data shown for AC3 Load. If other loading is used, refer to the load-life curves found in the product Technical Data. 2) B10 is known and 75% fail to open and 25% fail to close. B10d Fail to Open =B10x(1/75%), B10d Fail to Close =B10x(1/25%) 3) For Category greater than 1, diagnostic coverage must be supplied externally by direct monitoring of the mechanically linked auxiliary contacts. 4) Typical diagnostic test interval of 6 months. | Device Type 3 | Contactor |  |  | Output |  |  | 75 | 800000
Output Contactor: CAUS7-55: AC3 Load | Failure to close = dangerous fault | CAUS7-55 at AC3 | [5 empty] | 20 | 1) B10 Data shown for AC3 Load. If other loading is used, refer to the load-life curves found in the product Technical Data. 2) B10 is known and 75% fail to open and 25% fail to close. B10d Fail to Open =B10x(1/75%), B10d Fail to Close =B10x(1/25%) 3) For Category greater than 1, diagnostic coverage must be supplied externally by direct monitoring of the mechanically linked auxiliary contacts. 4) Typical diagnostic test interval of 6 months. | Device Type 3 | Contactor |  |  | Output |  |  | 25 | 800000
Output Contactor: CAUS7-60…97: Mechanical | Failure to open = dangerous fault | CAUS7-60…97 Mechanical | [5 empty] | 20 | 1) B10 Data shown is for no load, mechanical switching. 2) B10 is known and 50% fail to open and 50% fail to close. B10d Fail to Open =B10x(1/50%), B10d Fail to Close =B10x(1/50%) 3) For Category greater than 1, diagnostic coverage must be supplied externally by direct monitoring of the mechanically linked auxiliary contacts. 4) Typical diagnostic test interval of 6 months. | Device Type 3 | Contactor |  |  | Output |  |  | 50 | 6000000
Output Contactor: CAUS7-60…97: Mechanical | Failure to close = dangerous fault | CAUS7-60…97 Mechanical | [5 empty] | 20 | 1) B10 Data shown is for no load, mechanical switching. 2) B10 is known and 50% fail to open and 50% fail to close. B10d Fail to Open =B10x(1/50%), B10d Fail to Close =B10x(1/50%) 3) For Category greater than 1, diagnostic coverage must be supplied externally by direct monitoring of the mechanically linked auxiliary contacts. 4) Typical diagnostic test interval of 6 months. | Device Type 3 | Contactor |  |  | Output |  |  | 50 | 6000000
Standard product (non safety): D7 Push Buttons and Operators with Contacts | Standard | D7 | [5 empty] | 20 | 1) Products in this library are not specifically intended as safety devices, and the associated data represents reliability data. For this product, any use of the terms MTTFd, B10d, T10d or PFHd does not relate to a failure to danger. The user assumes all costs and liability for any decision on the use of this product in a safety application. 2) The use of simple electro-mechanical devices (such as Push Buttons or Selector Switches) is allowed in ISO 13849-1, Annex C. The designer must follow the ISO 13849-1 to ensure proper application and design of these devices in a safety-related part of a control system (SRP/CS). 3) Per Rockwell Automation Technical Data, the lowest mechanical and electrical life of this product is: B10 = 1,000,000 cycles. For simplified application, this data includes the combined Operator and Contact block assembly. 4) Applying the allowances in ISO 13849-1, Annex C, a 50% ratio of safe and dangerous failures is assumed. | Device Type 3 |  |  |  | Input |  |  | 50 | 1.0E6
Standard product (non safety): Contactor: CA7-9…55: Mechanical | Failure to close = dangerous fault | CA7-9…55 Mechanical | [5 empty] | 20 | 1) B10 Data shown is for no load, mechanical switching. 2) B10 is known and 50% fail to open and 50% fail to close. B10d Fail to Open =B10x(1/50%), B10d Fail to Close =B10x(1/50%) 3) For Category greater than 1, diagnostic coverage must be supplied externally by direct monitoring of the mechanically linked auxiliary contacts. 4) Typical diagnostic test interval of 6 months. | Device Type 3 | Contactor |  |  | Output |  |  | 50 | 13000000
Standard product (non safety): Contactor: CA7-9…37: AC3 Load | Failure to open = dangerous fault | CA7-9…37 at AC3 | [5 empty] | 20 | 1) B10 Data shown for AC3 Load. If other loading is used, refer to the load-life curves found in the product Technical Data. 2) B10 is known and 75% fail to open and 25% fail to close. B10d Fail to Open =B10x(1/75%), B10d Fail to Close =B10x(1/25%) 3) For Category greater than 1, diagnostic coverage must be supplied externally by direct monitoring of the mechanically linked auxiliary contacts. 4) Typical diagnostic test interval of 6 months. | Device Type 3 | Contactor |  |  | Output |  |  | 75 | 1300000
Standard product (non safety): Contactor: CA7-9…37: AC3 Load | Failure to close = dangerous fault | CA7-9…37 at AC3 | [5 empty] | 20 | 1) B10 Data shown for AC3 Load. If other loading is used, refer to the load-life curves found in the product Technical Data. 2) B10 is known and 75% fail to open and 25% fail to close. B10d Fail to Open =B10x(1/75%), B10d Fail to Close =B10x(1/25%) 3) For Category greater than 1, diagnostic coverage must be supplied externally by direct monitoring of the mechanically linked auxiliary contacts. 4) Typical diagnostic test interval of 6 months. | Device Type 3 | Contactor |  |  | Output |  |  | 25 | 1300000
Standard product (non safety): Contactor: CA7-9…55: Mechanical | Failure to open = dangerous fault | CA7-9…55 Mechanical | [5 empty] | 20 | 1) B10 Data shown is for no load, mechanical switching. 2) B10 is known and 50% fail to open and 50% fail to close. B10d Fail to Open =B10x(1/50%), B10d Fail to Close =B10x(1/50%) 3) For Category greater than 1, diagnostic coverage must be supplied externally by direct monitoring of the mechanically linked auxiliary contacts. 4) Typical diagnostic test interval of 6 months. | Device Type 3 | Contactor |  |  | Output |  |  | 50 | 13000000
Standard product (non safety): Contactor: CA7-43, 60, 72, 85, 97: AC3 Load | Failure to open = dangerous fault | CA7-43, 60, 72, 85, 97 at AC3 | [5 empty] | 20 | 1) B10 Data shown for AC3 Load. If other loading is used, refer to the load-life curves found in the product Technical Data. 2) B10 is known and 75% fail to open and 25% fail to close. B10d Fail to Open =B10x(1/75%), B10d Fail to Close =B10x(1/25%) 3) For Category greater than 1, diagnostic coverage must be supplied externally by direct monitoring of the mechanically linked auxiliary contacts. 4) Typical diagnostic test interval of 6 months. | Device Type 3 | Contactor |  |  | Output |  |  | 75 | 1000000
Standard product (non safety): Contactor: CA7-55: AC3 Load | Failure to open = dangerous fault | CA7-55 at AC3 | [5 empty] | 20 | 1) B10 Data shown for AC3 Load. If other loading is used, refer to the load-life curves found in the product Technical Data. 2) B10 is known and 75% fail to open and 25% fail to close. B10d Fail to Open =B10x(1/75%), B10d Fail to Close =B10x(1/25%) 3) For Category greater than 1, diagnostic coverage must be supplied externally by direct monitoring of the mechanically linked auxiliary contacts. 4) Typical diagnostic test interval of 6 months. | Device Type 3 | Contactor |  |  | Output |  |  | 75 | 800000
Standard product (non safety): Contactor: CA7-55: AC3 Load | Failure to close = dangerous fault | CA7-55 at AC3 | [5 empty] | 20 | 1) B10 Data shown for AC3 Load. If other loading is used, refer to the load-life curves found in the product Technical Data. 2) B10 is known and 75% fail to open and 25% fail to close. B10d Fail to Open =B10x(1/75%), B10d Fail to Close =B10x(1/25%) 3) For Category greater than 1, diagnostic coverage must be supplied externally by direct monitoring of the mechanically linked auxiliary contacts. 4) Typical diagnostic test interval of 6 months. | Device Type 3 | Contactor |  |  | Output |  |  | 25 | 800000
Standard product (non safety): Contactor: CA7-60…97: Mechanical | Failure to open = dangerous fault | CA7-60…97 Mechanical | [5 empty] | 20 | 1) B10 Data shown is for no load, mechanical switching. 2) B10 is known and 50% fail to open and 50% fail to close. B10d Fail to Open =B10x(1/50%), B10d Fail to Close =B10x(1/50%) 3) For Category greater than 1, diagnostic coverage must be supplied externally by direct monitoring of the mechanically linked auxiliary contacts. 4) Typical diagnostic test interval of 6 months. | Device Type 3 | Contactor |  |  | Output |  |  | 50 | 6000000
Standard product (non safety): Contactor: CA7-60…97: Mechanical | Failure to close = dangerous fault | CA7-60…97 Mechanical | [5 empty] | 20 | 1) B10 Data shown is for no load, mechanical switching. 2) B10 is known and 50% fail to open and 50% fail to close. B10d Fail to Open =B10x(1/50%), B10d Fail to Close =B10x(1/50%) 3) For Category greater than 1, diagnostic coverage must be supplied externally by direct monitoring of the mechanically linked auxiliary contacts. 4) Typical diagnostic test interval of 6 months. | Device Type 3 | Contactor |  |  | Output |  |  | 50 | 6000000
Standard product (non safety): Contactor: CA7-43, 60, 72, 85, 97: AC3 Load | Failure to close = dangerous fault | CA7-43, 60, 72, 85, 97 at AC3 | [5 empty] | 20 | 1) B10 Data shown for AC3 Load. If other loading is used, refer to the load-life curves found in the product Technical Data. 2) B10 is known and 75% fail to open and 25% fail to close. B10d Fail to Open =B10x(1/75%), B10d Fail to Close =B10x(1/25%) 3) For Category greater than 1, diagnostic coverage must be supplied externally by direct monitoring of the mechanically linked auxiliary contacts. 4) Typical diagnostic test interval of 6 months. | Device Type 3 | Contactor |  |  | Output |  |  | 25 | 1000000
Standard product (non safety): Electronic Coil for CAS6-115…300 Contactor | Standard | CAS6-115…300 Electronic Coil | [5 empty] | 20 | 1) Products in this part of the library are not specifically intended as safety devices, and the associated data represents reliability data. For this product, any use of the terms MTTFd, B10d, T10d or PFHd does not relate to a failure to danger. It relates only to a failure that results in the ON state of the outputs. The user assumes all costs and liability for any decision on whether a failure that results in the ON state of the outputs could be dangerous. 2) The MTTFd value for the electronic controlled coil must be added as a separate block or element when the interface function is used. 3) The data given applies to the following coil electronic codes: J, ZJ, Y, ZY, D, ZD, A, ZA, N. 4) If the contactor is used with the electronic interface selected it must be used in a redundant and monitored configuration for safety-related applications. 5) Subsystem channel must include this interface and the main power contactor. (2 blocks) | Device Type 2 |  | This product is not specifically intended as a safety device and the given data represents reliability data. Any use of the terms MTTFd, B10D, T10D or PFHd does not relate to a failure to danger. The user assumes all costs and liability for any decision to use these products as part of a functional safety-related system and on what represents a failure danger. |  | Output | 704

## Glossary
Symbol | Definition
B10D | Number of cycles until 10% of the components fail dangerously
PL | Performance Level
SIL | Safety Integrity Level
PFHD | Probability to dangerous failure per hour
TMT1 | Mission Time: Useful lifetime
MTTFD | Mean time to dangerous failure
MTTF | Mean time to failure
RDF | Ratio of dangerous failure as a percentage
B10 | Number of cycles until 10% of the components fail
DC | Diagnostic coverage
λDD | Dangerous detected failure rate
DFR | Dangerous failure rate
DTI | Diagnostic test interval (hours)
λDU | Dangerous undetected failure rate
HFT | Hardware Fault Tolerance
MTBF | Mean time between failure
PFDavg | At mission time of 20 years
λSD | Safe detected failure rate
SFF | Safe Failure Fraction
λS | Safe failure rate
SRT | Safety reaction time (milliseconds)
STR | Spurious trip rate
λSU | Safe undetected failure rate
T1 | Proof test interval in hours
TFR | Total failure rate